Section 230900 – INSTRUMENTATION AND CONTROL FOR HVAC

PART 1 – GENERAL

The following addition should be made to 1.2.B.

  - SUMMARY

- Related Sections include the following:

  - Division 23 Section “Hydronic Piping” for requirements for piping packages for control valves.

The following replaces the noted specification sections, except as noted.

  - ACTUATORS

- Electronic Actuators

    - Manufactured, brand labeled or distributed by BELIMO.

  - Size for torque required for damper seal at maximum design conditions and valve close-off pressure for system design.

  - Coupling: V-bolt dual nut clamp with a V-shaped, toothed cradle; directly couple and mount to the valve bonnet stem; or ISO-style direct-coupled mounting pad.

  - Mounting:  Actuators shall be capable of being mechanically and electrically paralleled to increase torque if required.

  - Overload protected electronically throughout rotation.

  - Fail Safe Operation:  Mechanical fail safe shall incorporate a spring-return mechanism.  Electronic fail safe shall incorporate an active balancing circuit to maintain equal charging rates among the Super Capacitors with a visual indication of the fail safe status on the actuator face with the power fail position field adjustable between 0 to 100% in 10o increments, a 2 sec [0-10 sec] <Insert Timing between 0-10 sec> operational delay, and capable of changing the fail-safe position through an integrated switch without removing the mounted actuator.

- Power Requirements: 24Vac/dc [120Vac] [230Vac]

- Proportional Actuators shall be software configurable through an EEPROM without the use of actuator mounted switches.  Programmable functions shall include a scalable operating range from 0.5 – 32.0 vdc with a 2.0 vdc (min) span; variable runtime; and data logging.

- Temperature Rating: -22 to +122ºF -30 to +50ºC [-58 to +122ºF -50 to +50ºC]

- Housing:  Minimum requirement NEMA type 2 (4/4X) / IP54 (IP67).

- Agency Listings:  ISO 9001, cULus, CE or CSA

- The manufacturer shall warrant all components for a period of 5 years from the date of production, with the first two years unconditional.

- Zone Valve Electronic Actuators  (SHOULD BE INCLUDED with 2.16.F. Zone Valves (two-position and modulating), below.)

    - Manufactured, brand labeled or distributed by BELIMO.

  - Size for torque required for valve close-off pressure for system design.

  - Coupling: Direct coupled to the valve body without the use of external devices or tools.

  - Overload protected electronically throughout rotation.

  - Fail Safe Operation:  Electronic fail safe shall incorporate an active balancing circuit to maintain equal charging rates among the Super Capacitors with the power fail position field adjustable between 0 to 100% in 10o increments, a 2 sec [0-10 sec] <Insert Timing between 0-10 sec> operational delay.

  - Flow Adjustment:  Flow capacity (Cv or gpm) shall be field adjustable without the use of external devices utilizing an integrated clip/scale assembly without removal of the actuator.  The control span shall adapt to the adjusted flow rating.

  - Power Requirements: 24Vac/dc [120Vac] [230Vac]

  - Auxiliary Switch:  1 SPST rated 1A at 30 VDC (resistive load) fully adjustable 0 to 100% of the actuator span.

  - Temperature Rating: 36 to 212ºF 2 to 100ºC ‘

  - Agency Listings:  ISO 9001, cULus, or CE.

  - The manufacturer shall warrant all components for a period of 5 years from the date of production, with the first two years unconditional.

- Industrial Actuators (SHOULD BE INCLUDED with 2.16.I. Butterfly Valves – Resilient Seat and 2.16.J. Butterfly Valves – High Performance for optional choices in actuation (e.g. – outdoor installations) by the bidder to meet project requirements.)

    - Manufactured, brand labeled or distributed by BELIMO.

  - The combination of valve and actuator shall meet the close-off requirements as specified in  Section 2.16.H – Butterfly Valves.

  - Overload Protection: An auto-reset thermal switch embedded in the motor.

  - Manual Override: Actuator shall be equipped with a hand wheel or shaft for manual override to permit operation of the actuator in the event of an electrical power failure

  - Power Requirements:  120VAC [24VAC] [230VAC] 1Ф.

  - Auxiliary Switches:  2 SPDT rated 3A at 250 VAC, pilot duty rated.

  - Temperature Rating: -22 to +150ºF.-30 to +65ºC.

  - Housing:  Minimum requirement NEMA type 4X/ IP67 with an industrial quality coating.  Actuator shall have an internal heater to prevent condensation within the housing.  A visual indication beacon shall indicate position status of the device.

  - Agency Listing:  ISO, CE, CSA

  - The manufacturer shall warrant for 2 years from the date of production.

  - CONTROL VALVES

- Manufacturer:

    - Manufactured, brand labeled or distributed by BELIMO.

- Control Valves:

  - Factory fabricated of type, body material, and pressure class based on maximum pressure and temperature rating of piping system, unless otherwise indicated.

  - Sizing:

    - Two-Position:  Line size or size using a pressure differential of 1 psi.

    - Two-Way Modulating:  [3 psid] 5 psid or twice the load pressure drop, whichever is more.

    - Three-Way Modulating:  Twice the load pressure drop, but not more than [3 psid]

5 psid.

[2.   Sizing (steam):

      - Two-Position:  Line size or sized using 10% of inlet gauge pressure.

      - Modulating:  15 PSIG or less inlet steam pressure, the pressure drop shall be 80% of inlet gauge pressure.  Higher than 15 PSIG inlet steam pressure the pressure drop shall be 42% of the inlet absolute pressure.]

Choose this option when specifying steam valves.

  - The control valve assembly shall be provided and delivered from a single manufacturer as a complete assembly.

- The manufacturer shall warrant all components for a period of 5 years from the date of production, with the first two years unconditional (except as noted).

- Pressure Independent Control Valves [Water Coil Optimization]  (Also, see 2.16.F.2 for Pressure Independent Zone Valves.)

  - NPS 2 and Smaller:  Forged brass body rated at no less than 250 PSI, stainless steel ball and stem, female NPT union ends, dual EPDM lubricated O-rings and a brass or TEFZEL characterizing disc.

  - NPS 2-1/2 through 6:  GG25 cast iron body according to ANSI Class 125, standard class B, stainless steel ball and blowout proof stem, flange to match ANSI 125  with a dual EPDM O-ring packing design, PTFE seats, and a stainless steel flow characterizing disc.

  - Accuracy:  The control valves shall accurately control the flow from 0 to 100% rated flow with an operating pressure differential range of 5 to 50 PSI differential across the valve with a valve body flow accuracy of +/- 5 total assembly error incorporating differential pressure fluctuation, manufacturing tolerances and valve hysteresis

  - Flow Characteristics:  Equal percentage characteristic.

- All actuators shall be capable of being electronically programmed in the field by use of external computer software or a dedicated handheld tool for the adjustment of flow.  Programming using actuator mounted switches or multi-turn actuators are not acceptable.

- [Water coil optimization shall be accomplished by utilizing a pressure independent control valve assembly; two temperature sensors providing feedback of coil inlet and outlet water temperatures; and an electronic flow meter to provide analog flow feedback.  Software shall control the valve to avoid the coil differential temperature from falling below a programmed set point, The valve assembly shall be capable of accepting an analog signal representing the coil power required.  Real-time data and configuration of valve operating parameters shall be available by means of BACnet MS/TP, BACnet/IP or HTTP. Monitored points shall include, but not be limited to inlet and outlet coil water temperatures, absolute flow, absolute valve position, absolute coil power and total heating/cooling energy in BTU/hr.  Configuration points shall include but not be limited to valve, flow, and power settings.  Historical trend data shall be stored for up to 13 months and be retrievable in a standard time-stamped format.]

- The manufacturer shall provide a published commissioning procedure following the guidelines of the National Environmental Balancing Bureau (NEBB) and the Testing Adjusting Balancing Bureau (TABB).

- A wet calibrated electronic flow meter shall provide dynamic feedback to measure flow and verify performance.

- The control valve shall require no maintenance and shall not include replaceable cartridges.

When choosing pressure independent control valves, specifier must include the revisions to 232113 for elimination of the balancing valve installation.  Modify 230593 to eliminate the individual balancing of each coil/valve combination when installing pressure independent valves.

- Characterized Control Valves:

- 3” and Smaller:  Nickel-plated forged brass body rated at no less than 400 psi, stainless steel ball and blowout proof stem, female NPT end fittings, with a dual EPDM O-ring packing design, fiberglass reinforced Teflon seats, and a TEFZEL or stainless steel flow characterizing disc.

- 2-1/2” through 6”:  GG25 cast iron body, ANSI 125, class B, stainless steel ball and blowout proof stem, flange to match ANSI 125 with a dual EPDM O-ring package design, PTFE seats, and a stainless steel flow characterizing disc.

- Valve assemblies shall be maintenance free.

- NPS 2” and smaller characterized control valves shall be provided as part of a pipe package supplied by the valve manufacturer.  The supply side of the coil shall contain a strainer/shut-off ball valve/drain [an integrated isolation ball valve/manual air vent] with a P/T port.  The return side of the coil shall contain a union fitting with a P/T port, characterized control valve, an integrated manual balancing valve/union/isolation ball valve/manual air vent with P/T port.  Shut-off valves as an integrated part of the characterized control valve are prohibited.  [For 3-way installations, supply an integrated 100% port isolation valve/manual air vent with a P/T port for field installation in the bypass of the circuit.]  . [A [12”] [24”] flexible hose set shall be provided for each coil supply and return connection for all pipe packages.]

- [Six-way characterized control valves for changeover applications on combination heating/cooling chilled beams shall have the following characteristics:

  - NPS ½” and ¾”:  Nickel plated forged brass body rated at no less than 600 psi, dual chrome plated brass ball and blowout proof stems, and female NPT end fittings. Each three-way portion of the 6-way valve body shall have EPDM O-Ring packing design, Teflon PTFE seats, and an chrome plated steel characterizing disc.

  - The six-way control valve shall be controlled by a rotary actuator for managing two media in a switching application with a linear flow characteristic.  The valve shall be closed to flow at mid-rotation.]

- Zone Valves (two-position and modulating)

  - Non-Pressure Independent Zone Valve

- NPS ½” and ¾”:  Forged brass body rated at no less than 230 psi, chrome plated brass ball and stem, NPT female ends and EPDM O-rings.  Valves utilizing flapper or paddle assemblies for flow control shall not be permitted.

  - Pressure Independent Zone Valve

- NPS ½”:  Forged brass body rated at no less than 360 PSI, stainless steel ball and stem, ball shall be designed with a characterizing feature no inserted discs, female NPT union ends, and dual EPDM lubricated O-rings.

- Accuracy:  The control valves shall accurately control the flow from 0 to 100% rated flow with an operating pressure differential range of 5 to 50 PSI differential across the valve with a valve body flow accuracy of +/- 5% total assembly error incorporating differential pressure fluctuation, manufacturing tolerances and valve hysteresis.

- The manufacturer shall provide a published commissioning procedure following the guidelines of the National Environmental Balancing Bureau (NEBB) and the Testing Adjusting Balancing Bureau (TABB).

  - Flow Characteristic:  Equal percentage (2-way) and Linear (3-way).

  - Flow rating (Cv or gpm max) shall be field adjustable without the use of external devices.  The control span shall adapt to the adjusted flow rating.

  - The control valve shall require no maintenance and shall not include replaceable cartridges.

- Globe valves shall have the following characteristics:

  - NPS 2 and Smaller:  ANSI Class 250 bronze body, stainless steel stem, brass plug, bronze seat, and a TFE packing.

  - NPS 2-1/2 and Larger:  ANSI Class 125 [250] cast iron body, stainless steel stem, bronze plug, bronze seat, and a TFE V-ring packing.

  - Flow Characteristics:  Two-way valves shall have equal percentage characteristics; three-way valves shall have linear characteristics.

  - Two- and three-way globe valves shall be used only if characterized control valves do not fit the sizing criteria or application.

[Steam system globe valves shall have the following characteristics:

  - NPS 2 and Smaller:  ANSI Class 250 bronze body; stainless steel seat, stem and plug; and a TFE packing.

  - NPS 2-1/2 and Larger:  ANSI Class 125 [250] cast iron body; stainless steel seat, stem and plug; and a TFE V-ring packing.

  - Flow Characteristics:  Linear or equal percentage characteristics.]

Choose option when specifying globe valves in a steam system application.

- Butterfly Valves – Resilient Seat:

  - NPS 2 to 12:  Valve body shall be full lugged ductile iron 200 psig body with a 304 stainless steel disc, EPDM seat, extended neck and shall meet ANSI Class 125/150 flange standards.   Disc-to-stem connection shall utilize an internal spline.  The shaft shall be supported at four locations by RPTFE bushings.  A coated disc shell is not acceptable.

  - NPS 14 and Larger:  Valve body shall be full lugged ductile iron 150 psig body with a 304 stainless steel disc, EPDM seat, extended neck and shall meet ANSI Class 125/150 flange standards.  Disc-to-stem connection shall utilize a dual-pin method to prevent the disc from settling onto the liner.  The shaft shall be supported at four locations by RPTFE bushings.  A coated disc shell is not acceptable.

  - Sizing:  Two-Position (on/off) butterfly valves shall be sized using the 900 Cv

rating.  Modulating butterfly valves shall be sized using the 600 Cv rating.

  - Flow Characteristics:  Modified equal percentage, unidirectional dead end service.

  - Close-Off Pressure Rating:  Bubble-tight shutoff (no leakage).

  - The combination of two 2-way butterfly valves in a tee configuration cross-linked to ensure proper flow orientation shall be permitted.  The tee shall be constructed of cast iron/stainless steel.

- Butterfly Valves – High Performance:

  - Valve body shall be full lugged carbon steel ANSI Class 150 [300] body with a 316 stainless steel disc without a nylon coating, RTFE seat, and be ANSI Class 150300 flange standards.   Blowout-proof shaft shall be 17-4ph stainless steel and shall be supported at four locations by glass-backed TFE bushings.  Valve packing shall be Chevron TFE and shall include fully adjustable packing flange and separable packing gland.  Valve body shall have long stem design to allow for 2” insulation (minimum).  Valve face-to-face dimensions shall comply with API 609 and MSS-SP-68.  Valve assembly shall be completely assembled and tested, ready for installation.

  - Sizing:  Two-Position (on/off) butterfly valves shall be sized using the 900 Cv

rating.  Modulating butterfly valves shall be sized using the 600 Cv rating.

  - Flow Characteristics:  Modified equal percentage, full rated, bi-directional,

dead end service with either flange removed.

  - Close-Off Pressure Rating:  Bubble-tight shutoff (no leakage).

  - Media Temperature Range: ANSI Class 150 [300] limitations.

  - Max Differential Pressure:  285 psi @ 100 deg F for ANSI 150 (725 psi @ 100 deg F for ANSI 300).

  - The combination of two 2-way butterfly valves in a tee configuration cross-linked to ensure proper flow orientation shall be permitted.  The tee should be constructed of cast iron/stainless steel.

Select 2.16.B. Industrial Actuators as an additional actuator option when specifying 2.16.G Butterfly Valves – Resilient Seat and 2.16.H Butterfly Valves – High Performance.)

To be inserted into Section 233300 – AIR DUCT ACCESSORIES

  - SMOKE DAMPERS

I.  Damper Motors:

  - Manufactured, brand labeled or distributed by BELIMO.

  - Size for torque required for damper seal at load conditions with one actuator per damper section.  .Mechanically paralleled or ‘piggybacked’ actuators are not permitted.

  - Coupling: V-bolt dual nut clamp with a V-shaped toothed cradle.  Aluminum clamps or set screws are not acceptable.

  - Overload Protection: Microprocessor or an electronic based motor controller providing burnout protection if stalled before full rotation is reached.  The actuator shall be electronically cut off at full open to eliminate noise generation with the holding noise level to be inaudible.

  - Power Requirements: 0.23A (running) and 0.09A (holding) at 24V-ac or 27 VA (running) and 10 VA (holding) at 120V-ac.

  - Actuator timing shall be 15 sec [75 sec] [local codes].

  - Temperature Rating: Actuator shall have a UL555S listing by the damper manufacturer for 350ºF [250ºF].

  - [Proportional Smoke Damper Actuators shall meet all requirements specified above and shall modulate 0-100% open in response to a 2-10vdc or 4-20mA control signal.  A 2-10vdc feedback output shall provide a 2-10vdc signal for position indication.

- Power Requirements (Proportional): Maximum (running) 12 VA at 24-V ac or 8 W at 24-V dc.  Maximum (holding) 5VA at 24-V ac or 3 W at 24-V dc.

- A manual override winder and locking mechanism shall be provided for override operation of the actuator on a loss of power.]

  - [Balancing Smoke Damper Actuators shall meet all requirements specified above and shall include an integral adjustable maximum opening potentiometer for airflow adjustment.

- Power Requirements (Balancing):  Maximum (running) 9.5 VA at 24-V ac or 6 W at 24-V dc.  Maximum (holding) 5VA at 24-V ac or 3 W at 24-V dc.

- A manual override winder and locking mechanism shall be provided for override operation of the actuator on a loss of power to the actuator.]

The following replaces item 2.8.K.1

- Auxiliary switches for [signaling] [fan control] [or] [position indication].

2.9	COMBINATION FIRE AND SMOKE DAMPERS

O.  Damper Motors:

- Manufactured, brand labeled or distributed by BELIMO.

- Size for torque required for damper seal at load conditions.

- Coupling: V-bolt dual nut clamp with a V-shaped toothed cradle.  Aluminum clamps or set screws are not acceptable.

- Overload Protection: Microprocessor or an electronic based motor controller providing burnout protection if stalled before full rotation is reached.  The actuator shall be electronically cut off at full open to eliminate noise generation with the holding noise level to be inaudible.

- Power Requirements: 0.23A (running) and 0.09A (holding) at 24V-ac or 27 VA (running) and 10 VA (holding) at 120V-ac.

- Actuator timing shall be 15 sec [75 sec] [local codes].

- Temperature Rating: Actuator shall have UL555 and UL555S listings by the damper manufacturer for 350ºF [250ºF].

- [Proportional Combination Fire and Smoke Damper Actuators shall meet all requirements specified above and shall modulate 0-100% open in response to a 2-10vdc or 4-20mA control signal.  A 2-10vdc feedback output shall provide a 2-10vdc signal for position indication.

- Power Requirements (Proportional): Maximum (running) 12 VA at 24-V ac or 8 W at 24-V dc.  Maximum (holding) 5VA at 24-V ac or 3 W at 24-V dc.

- A manual override winder and locking mechanism shall be provided for override operation of the actuator on a loss of power.]

- [Balancing Combination Fire and Smoke Damper Actuators shall meet all requirements specified above and shall include an integral adjustable maximum opening potentiometer for airflow adjustment.

- Power Requirements (Balancing):  Maximum (running) 9.5 VA at 24-V ac or 6 W at 24-V dc.  Maximum (holding) 5VA at 24-V ac or 3 W at 24-V dc.

- A manual override winder and locking mechanism shall be provided for override operation of the actuator on a loss of power to the actuator.]

The following replaces item 2.9.Q.1

- Auxiliary switches for [signaling] [fan control] [or] [position indication].

- Housing:  Steel housing, aluminum is unacceptable.

- Agency Listing:  ISO 9001, UL873, or UL60730.

- The manufacturer shall warrant all components for a period of 5 years from the date of production, with the first two years unconditional.

NOTE TO SPECIFIER

Any (or all) of the following manufacturers are listed per UL555S with Belimo actuators:  Air Balance, Arlan, E.H. Price, Greenheck, Leader, Lloyd Industries, Nailor, Pottorff, Prefco, Ruskin and Safe-Air.

Section 237413 – PACKAGED, OUTDOOR, CENTRAL-STATION AIR-HANDLING UNITS

The following replaces paragraphs 2.10.C.11 and 2.10.C.12.

  - CONTROLS

- Controller

- Economizer Outdoor-Air Damper Operation:

  - Manufactured, brand labeled or distributed by BELIMO.

  - Economizer shall be capable of single dry bulb, differential dry bulb, single enthalpy or differential enthalpy control strategy, as required, per ASHRAE 90.1. Sensing devices shall be non-proprietary.

  - ASHRAE Climate Zone selection for high limit setting shall be through entry of the installed location zip code through the MMI without the use of printed documentation.

  - The device shall incorporate brownout protection that will prevent the compressors from operating in low voltage conditions while remaining in control.  Upon startup from a brownout or blackout condition the unit shall provide automatic random on to prevent electrical surge from multiple compressor starting.

  - Alarms for fault detection and diagnostics shall be indicated by both a visual LED indicator and text description accessible through the MMI.  Current and historical alarms (including elapsed time since occurrence) shall be accessible via the MMI.  Upon sensor failure the economizer shall automatically detect the proper economizer sequence to maintain control.

  - Device shall be compliant with the latest version of the following energy codes:  ASHRAE 90.1, CA Title 24, and NECB.

  - The manufacturer shall warrant all components for a period of 5 years from the date of production, with the first two years unconditional.

  - Occupied Periods.

    - Open to [10] [25] <Insert percent>percent fixed minimum intake and maximum 100 percent of the fan capacity to comply with ASHRAE 90.1.  Controller shall permit air side economizer operation when outdoor air is below the outdoor air temperature/enthalpy as determined by entry of the installed location zip code on the integrated display.

    - Economizer dampers shall be capable of being sequenced with the mechanical cooling system and be capable of providing a partial cooling load with the mechanical cooling.

    - The outdoor air intake minimum position shall automatically reduce upon reaching a predetermined high limit setpoint.  When outdoor air is 100% and the mechanical cooling is enabled the outdoor air damper shall close to reduce freeze conditions if required.

  - Unoccupied Periods.

    - Close outdoor air damper and open return air damper.

  - [Carbon Dioxide Sensor Operation.

    - Occupied Periods.  Reset minimum outdoor air down to minimum [10] <Insert percent> percent to maintain maximum concentration per ASHRAE 90.1

    - Unoccupied Periods:  Close outdoor air damper and open return air damper.]

# Text boxes

SPECIFYING PRESSURE INDEPENDENT CONTROL VALVES REQUIRE THE FOLLOWING ADDITIONS TO SECTIONS 232113 AND 230593.

To be inserted into Section 232113 – HYDRONIC PIPING

  - CONTROL VALVES

K.  Calibrated Balancing Valves and Automatic Flow-Control Valves shall not be used on equipment where pressure independent control valves are installed.

To be inserted into Section 230593 – TESTING, ADJUSTING, AND BALANCING FOR HVAC

  - PROCEDURE FOR HYDRONIC SYSTEMS

- Systems installed with pressure independent control valves shall not require terminal level hydronic system balancing.  [Field verify installation and operating differential pressure range of all pressure independent control valves.] [Total system flow shall be verified to be within +/-10% of system design.] [10%] [20%] [25%] <Insert Percentage> of the total installed product shall be randomly checked for individual conformance.  Exact locations of tested product to be coordinated with the design engineer.]  Any individual adjustments for the pressure independent valve assembly (valve and actuator combination) for field conditions shall be performed using the pressure independent control  valve manufacturer’s documented procedure following the guidelines of the National Environmental Balancing Bureau (NEBB) and the Testing Adjusting Balancing Bureau (TABB)]